## IPI DRB Minutes
|  | IBIDEN PHILIPPINES, INC. | [17 empty] | DRB/MRB No. : |  | D-CORE-19-10-005
|  | DRB/MRB REPORT MINUTES | [17 empty] | RFC No. : |  | 05-1019-0030
Theme: |  |  | Earth Leakage Alarm Resulted to No Circulation of E-less bath
Meeting Date : |  |  | 22-Oct-19 | [11 empty] | Originated by : |  |  |  | Teody Barba Jr. / CORE1
Meeting Time: |  |  | Start: 1530h | [16 empty] | Name /Block
Meeting Place: |  |  | CORE Meeting Area | [11 empty] | Approved by : |  |  |  | Virgie Mendoza
Chairman: |  |  | Teody Barba | [15 empty] | Originator ASM/SM/DGM/GM
Block: |  |  | CORE
Attendees : |  |  | Manufacturing |  |  | Engineering/NPD |  |  | Facilities/EE |  |  |  |  | QA/QC |  |  |  |  | PPIC/CSE |  |  |  | Other
|  |  | Teody |  |  | Raysa B. |  |  | S' Nanie |  |  |  |  | Arnel
|  |  | Virgie San |  |  | Neil
Mizuno San
<1>PROBLEM STATEMENT : (Put another sheet if multiple lots was discovered affected)
DEFECT ISSUE: |  |  | Earth Leakage Alarm Resulted to No Circulation of E-less bath |  | # | PRODUCT/MODEL AFFECTED |  |  | PRODUCT FAMILY |  |  | LEDGER NO. |  | PRODUCT SIZE |  | LOT NUMBER |  |  | AFFECTEDLAYER |  | AFFECTED PANEL |  | AFFECTED UNIT OR IF PERCENTAGE
DATE/TIME OCCURRED: |  |  | Oct-21-19 |  | 1 | IPI Coffeelake BGA Halo 6+2 |  |  | BGA14 |  |  | 00138-00 |  | 27 X 27 |  | P7909020 |  |  | 1st |  | 1-8 |  | N/A
PROCESS DETECTED: |  |  | Desmear |  | 2 | Cougar Mountain |  |  | BGA15 |  |  | 774-8787 |  | 27 X 27 |  | P7910460 |  |  | 1st |  | 1-32 |  | N/A
PROCESS AFFECTED: |  |  | Desmear |  | 3
# OF AFFECTED LOTS : |  |  | 2 |  | 4
WHO DETECTED: |  |  |  |  | 5
6
WHAT IS THE PROBLEM DIFFERENCE FROM NORMAL TO ABNORMAL SITUATION? CHANGING POINT? DISCUSS THE FLOW. (Indicate 5W and 1H)
THE AGENDA ITEM IS RECURRENCE? |  |  |  | RECURRENCE |  |  | NEW |  |  |  | Recurrence Definition |  |  |  | 1. Rootcause is clear happened in same MC and parts 2. Rootcause is not clear but same issue 3. The Action was not proliferated to other process and machine but it was discussed during the meeting
THE AGENDA ITEM IS ESCAPEE? |  |  |  | YES |  |  | NO
PROBLEM CATEGORY |  |  | MAN |  | MACHINE |  |  | METHOD |  |  | MATERIAL |  |  | MEASUREMENT |  |  |  | ENVIRONMENT |  |  |  | OTHERS
DRB CLOSING RANK |  |  | RANK 1 |  | RANK 2 |  |  | RANK 3 |  |  | RANK 4 |  |  | RANK 5 |  |  |  | OTHERS
<2> INVESTIGATION/IDENTIFICATION OF AFFECTED AREA, SITUATION (Define the phenomenon, mode and tendency occurrence,Etc.)
1 | 0550h DCP1 C - shift encountered Line p/lb: Alarm! Fault of earth leakage breaker 3
2 | 2 lots were inside the machine. 1 lot (P7910460 Cougar Mountain) and 8 panels (P7909020 IPI Coffeelake BGA Halo).
3 | During alarm, noticed that the panel on E-less were not submerged into solution (no circulation) but cv still running.
4 | Upon unloading noticed that panels affected has Cu undeposition.
5 | Observed high temperature inside DCP1 Control panel due to Cooling System already defective
<3> CONTAINMENT ACTION (Note: Do not disable the interlock system when doing the action) | [15 empty] | Responsible |  |  | Completion Date |  |  | Status
Name / Block
1. Stop loading. | [15 empty] | MFG Edwin |  |  | 2019-10-21
2. FAC try to replaced Interface module at KB60 | [15 empty] | FAC Kenneth |  |  | 2019-10-21 |  |  | DONE. Alarm still cannot reset
3. Conduct additonal checking and ISOLATION by FAC and Maker | [15 empty] | FAC Sir Nanie |  |  | 2019-10-21 |  |  | Done. No problem on direct starters.
<4> DISPOSITION OF AFFECTED LOT AND RISK ASSESSMENT
Assessment Item (# of sample/Method) |  |  |  | Responsible Name / Block |  |  | Completion Date |  |  | Assessment Result (No Good/TTL QTY) | [5 empty] | Judgment (OK/NG) |  |  | Final Disposition
Check panel appearance after Unloading |  |  |  | MFG Jez |  |  | 2019-10-21 |  |  | 1 lot and 8 panels with Cu undepo | [5 empty] | NG
Crosscut 2 Panels for Cu Undepo verification. |  |  |  | QC Arnel |  |  | 2019-10-21 |  |  | with cu undepo (confirmed) | [5 empty] | NG |  |  |  | Proceed
[20 empty] | Piece Out |  | Qty : ______________________________
[20 empty] | Sheet Out |  | Qty : ____8___ Pnl #: _1-8 (P7909020)_
[20 empty] | Lot Out |  | Qty : ____1 lot (P7910460)_____________
[20 empty] | SDR |  | Qty : ______________________________
Risk Assessment Category | [10 empty] | Remarks
|  | Low |  | Medium |  |  |  | High |  |  | ________________________
<5>ACTION REQUIRED (Note: Do not disable the interlock system when doing the action)
Action Request | [9 empty] | Responsible Name / Block | [5 empty] | Completion Date |  |  | Detail Results
1. Replacement of DCP#1 Control panel cooling system (3 units) | [9 empty] | FAC Nanie | [5 empty] | ww01
2. Replacement of ALL Power module | [9 empty] | FAC Nanie | [5 empty] | ww52
<6> ROOTCAUSE GENERATION/ANALYSIS <WHY ANALYSIS by 5M1E, DESIGN AND CAPABILITY>
1. FACTOR GAP ANALYSIS
| Problem/Issue |  | Gap Type |  | 1st why |  |  |  | 2nd why | [5 empty] | 3rd why | [5 empty] | 4th why |  |  | 5th why
| Earth Leakage Alarm Resulted to No Circulation of E-less bath |  | Technical |  | Slave 10 module tripped-off |  |  |  | Defective power module | [5 empty] | Electrical failure | [5 empty] | Long TIME Usage (13 yrs usage)
Systemic
Detection
2. FINAL ROOT CAUSE and MECHANISM OF AFFECTED ISSUE
Defective electrical component of Power module due to long time usage
<7> CORRECTIVE ACTION | [12 empty] | Responsible |  |  |  | Completion Date |  |  | Status |  |  | Need CN & DR?
[13 empty] | Name / Block | [9 empty] | Yes | No
1. Replacement of Power Module | [12 empty] | FAC S'Nanie |  |  |  | WW43.1 |  |  |  | DONE |  |  | √
<8> PREVENTIVE ACTION | [12 empty] | Responsible |  |  |  | Completion Date |  |  | Status |  |  | Need CN & DR?
[13 empty] | Name / Block | [9 empty] | Yes | No
1. Change maintenance from CBM to TBM (every 10 yrs) and include on PIS | [12 empty] | FAC S'Nanie |  |  |  | ww43.3 |  |  |  | Open |  |  | √
<9> PROLIFERATION | [15 empty] | Responsible |  |  | Completion |  |  | Status
[16 empty] | Name / Sign |  |  | Date
Product |  | Block | Process/line |  | Machine |  | Proliferate Item
1
2
<10>AMOUNT OF LOSS . The total sum______$795.61___________
Product |  |  |  |  | Unit Qty | [7 empty] | Amount of Loss | [6 empty] | Remarks
Cougar Mountain |  |  |  |  | 7168 | [7 empty] | 617.05
IPI Coffeelake BGA Halo 6+2 |  |  |  |  | 1152 | [7 empty] | 178.56
<11> CLOSING APPROVAL (The approver person in charge should put details of the validation and closing confirmation result)
The Validation activity | [16 empty] | Closing Approver |  |  |  |  | Closing Date
DGM Nobuyuki Ito
QA-SCAR-MRB-02-00-01 Rev. 11